The Zone Expand-er is a buffer device that is switched on the one hand between the contacts or sensor switches and on the other hand it is connected to the zone inputs of the alarm system burglary or access control systems.

The role of the device is to replace the constant load voltage of the loop with a voltage with random voltages in the range of 6 to 11 V. Such a solution contributes to the improvement of the protection level, because compromising the variability of voltages changing randomly is extremely difficult compared to compromising voltages with a constant value in

On the output side, this device simply simulates the current loop as in a classic constant voltage circuit reflecting open / close contact, cut wire and short loop states.

The device supports two zones loops input.
The power supply of the device should be from UL / ULC listed power supplier for Burglar Alarm Systems or from the control of the zones input of the alarm system,

From the input side, a signal loop is connected to the Zone 1 In / Zone 2 IN inputs and the COMMON terminal, with zone loop having two series-connected EOL resistors, one of which is connected in parallel with the contact, see DWG 1.
In case when the zone loop is terminated with only one EOL resistor connected in parallel with the contact, it should be connected to the terminal Z1 IN / w R1 / (Z2 IN in R1 ') and the common input. Resistor R2 connected in series in complex loop is then connected to terminals R1 / R2, see DWG 1A.

The Ohm value of the auxiliary resistors in series with the resistor in the EOL loop should be + / _ 5% of the EOL resistors.
A reference resistor with the value of Ohm equal to the measured resistance complex loop is connected to the R REf1 / R Ref2 inputs with the door closed, the window or the sensor (PIR) inactive.

EOL resistors can be the same already installed in an existing complex loop. In order to make the compromise more difficult, the EOL resistors can be changed to any value from the 2k to 5.6k range, while the R Rf R1 / R Ref 2 resistors must be selected according to the new resistance and a complex loop with closed door, window or inactive PIR. Also in the case of a single EOL resistor, the additional series resistor R1 / R1 'must accordingly have the same value as the new EOL resistor.

The contact state with closed door, window or PIR can be NO or NC. Notwithstanding the above, the resistor R Ref must reflect the negative loop resistance at the door, window-closed or PIR inactive. When a zone loop has only one EOL resistor, ten parallel connected contact should be NO for a close door, window or PIR in inactive state.

The GND terminal connects the COMMON circuit with the GND circuit through a capacitor with a capacity of 100 nF.
It can be connected to GND to reduce the effects of electromagnetic interference.

On the output side of the device, two EOL resistors with the value provided for the existing alarm system should be connected. One of them will be connected internally in parallel with the simulated electronics contact. If the installed system requires only one EOL resistor, a jumper must be installed instead of EOL R1 / EOL R1 '. The To Zonne1 / To Zone 2 and COMMON terminals are connected to the Input complex of the installed system, the TAMPER 1 terminal can be used for serial connection to To Zone 1 or Zone 2 and the Tamper 2 terminal to the alarm system zone input. There is only one contact tamper and it can be used as a serial connection to the To Zone 1 or Zone 2 output or as an individual Tamper 1 / Tamper 2 output.
To the 12V- PS and 12V + PS terminals, connect the 12V power supply with the capacity of at least 50 mA.
In the event of a fault, short circuit of the internal device, the device output will be in a state corresponding to an opposing loop.

In the event of a complex loop over voltage caused by a close discharge from a lightning strike, the zone system temporarily blocks the change of state at the outputs within the time range up to 200 u u sec.